## LineUp
Models Line Up
Indoor Unit
Category | Picture | Chassis | Nominal Capacity (kBtu/h) | Model Name
Deluxe |  | S1 | 12 | NH12SP.NS1 (S3NW12121CA.EC6GEEU)
Deluxe |  | S1 | 9 | NH09SP.NS1 (S3NW09121CA.EC6GEEU)
Outdoor Unit
Power Supply | Picture | Chassis | Nominal Capacity (kBtu/h) | Model Name
1 Ø, 220 ~ 240 V, 50 Hz |  | U24A | 12 | NH12SP.U24A (S3UW12121CA.EC6GEEU)
1 Ø, 220 ~ 240 V, 50 Hz |  | U24A | 9 | NH09SP.U24A (S3UW09121CA.EC6GEEU)

## Spec
Specifications
Buyer Model | Set (Indoor / Outdoor) |  | Unit | NH12SP.SS1 (NH12SP.NS1/NH12SP.U24A) |  |  | NH09SP.SS1 (NH09SP.NS1/NH09SP.U24A)
Factory Model |  |  |  | S3-W12121CA.EC6GEEU (S3NW12121CA.EC6GEEU/S3UW12121CA.EC6GEEU) |  |  | S3-W09121CA.EC6GEEU (S3NW09121CA.EC6GEEU/S3UW09121CA.EC6GEEU)
Capacity | Cooling | Min ~ Rated ~ Max | kW | 0.900 | 3.500 | 4.350 | 0.900 | 2.500 | 4.000
|  |  | Btu/h | 3,073 | 11,950 | 14,853 | 3,073 | 8,536 | 13,658
|  |  | kJ/h | 3,240 | 12,600 | 15,660 | 3,240 | 9,000 | 14,400
| Cooling (T3) | Min ~ Rated ~ Max | kW | - | - | - | - | - | -
|  |  | Btu/h | - | - | - | - | - | -
| Heating | Min ~ Rated ~ Max | kW | 0.900 | 4.000 | 6.200 | 0.900 | 3.200 | 5.700
|  |  | Btu/h | 3,073 | 13,658 | 21,169 | 3,073 | 10,926 | 19,462
|  |  | kJ/h | 3,240 | 14,400 | 22,320 | 3,240 | 11,520 | 20,520
| Heating -7 °C | Max | kW | 5.000 |  |  | 4.500
Power Input | Cooling | Min ~ Rated ~ Max | W | 200 | 774 | 1,600 | 200 | 475 | 1,500
| Cooling (T3) | Min ~ Rated ~ Max | W | - | - | - | - | - | -
| Heating | Min ~ Rated ~ Max | W | 190 | 830 | 2,000 | 190 | 610 | 1,600
Running Current | Cooling | Min ~ Rated ~ Max | A | 1.80 | 6.00 | 9.00 | 1.80 | 3.80 | 8.10
| Cooling (T3) | Min ~ Rated ~ Max | A | - | - | - | - | - | -
| Heating | Min ~ Rated ~ Max | A | 1.70 | 6.30 | 10.00 | 1.70 | 4.80 | 9.00
EER |  |  | W/W | 4.52 |  |  | 5.26
|  |  | (Btu/h)/W | 15.44 |  |  | 17.97
|  |  | (kJ/h)W | 16.28 |  |  | 18.95
EER (T3) |  |  | W/W | - |  |  | -
|  |  | (Btu/h)/W | - |  |  | -
SEER |  |  | - | 8.7 |  |  | 8.8
COP |  |  | W/W | 4.82 |  |  | 5.25
|  |  | (Btu/h)/W | 16.45 |  |  | 17.91
|  |  | (kJ/h)W | 17.35 |  |  | 18.89
SCOP |  |  | - | 4.6 |  |  | 4.6
P design C / P design H |  |  | kW | 3.5 / 3.8 |  |  | 2.5 / 3.8
Energy Label Grade |  | Cooling / Heating | - | A+++ / A++ |  |  | A+++ / A++
Annual Energy Consumption |  | Cooling / Heating | kWh/year | 140.8 / 1156.3 |  |  | 99.4 / 1156.3
Weighted ERR |  |  | (Btu/h)/W | - |  |  | -
|  |  | WW | - |  |  | -
Power Supply |  |  | Ø, V, Hz | 1, 220 ~ 240, 50 |  |  | 1, 220 ~ 240, 50
Available Voltage Range |  |  | V | 187 ~ 276 |  |  | 187 ~ 276
Power Factor |  | Cooling / Heating | % | 97.0 / 97.0 |  |  | 97.0 / 97.0
Moisture Removal |  |  | l/h | 1.30 |  |  | 1.15
Indoor | Air Flow Rate | Cooling, SH / H / M / L | m³/min | 13.6 / 10.5 / 8.1 / 5.7 |  |  | 13.6 / 10.5 / 8.1 / 5.7
|  | Heating, SH / H / M / L | m³/min | 14.2 / 10.5 / 8.1 / 5.7 |  |  | 14.2 / 10.5 / 8.1 / 5.7
| Sound Pressure Level | Cooling, SH / H / M / L / SL | dB(A) | 47 / 40 / 35 / 27 / 19 |  |  | 47 / 40 / 35 / 27 / 19
|  | Heating, SH / H / M / L | dB(A) | 48 / 40 / 35 / 27 |  |  | 48 / 40 / 35 / 27
| Sound Power Level |  | dB(A) | 60 |  |  | 60
| Dimensions (W × H × D) | Net | mm | 895 x 307 x 235 |  |  | 895 x 307 x 235
|  | Shipping | mm | 967 x 383 x 296 |  |  | 967 x 383 x 296
| Weight | Net | kg | 12.3 |  |  | 12.3
|  | Shipping | kg | 14.8 |  |  | 14.8
| Exterior Color Code |  | - | Munsell 7.5P 9/2 (RAL 9003) |  |  | Munsell 7.5P 9/2 (RAL 9003)
Outdoor | Air Flow Rate | Max | m³/min | 49.0 |  |  | 49.0
| Fan Motor Speed | Cooling, Min ~ Max | rpm | 190 ~ 660 |  |  | 190 ~ 660
|  | Heating, Min ~ Max | rpm | 190 ~ 710 |  |  | 190 ~ 710
| Sound Pressure Level | Cooling, Rated | dB(A) | 49 |  |  | 49
|  | Heating, Rated | dB(A) | 51 |  |  | 51
| Sound Power Level |  | dB(A) | 65 |  |  | 65
| Dimensions (W × H × D) | Net | mm | 870 x 650 x 330 |  |  | 870 x 650 x 330
|  | Shipping | mm | 1026 x 683 x 446 |  |  | 1026 x 683 x 446
| Weight | Net | kg | 43.800 |  |  | 43.800
|  | Shipping | kg | 47.400 |  |  | 47.400
| Max. Fuse Size |  | A | 20.000 |  |  | 20.000
| Exterior Color Code |  | - | Munsell 9.54Y 8.34/1.31 (RAL 9001) |  |  | Munsell 9.54Y 8.34/1.31 (RAL 9001)
| Operation Range | Cooling | °C DB | -15 ~ 48 |  |  | -15 ~ 48
|  | Heating | °C DB | -35 ~ 24 |  |  | -35 ~ 24
|  | Heating | °C WB | -35 ~ 18 |  |  | -35 ~ 18
Circuit Breaker |  |  | A | 25 |  |  | 25
Power Supply Cable |  |  | No. × mm² | 3 x 2.5 |  |  | 3 x 2.5
Power Supply to Unit |  |  | - | Outdoor |  |  | Outdoor
Power and Communication Cable |  |  | No. × mm² | 4 x 1 |  |  | 4 x 1
Piping | Size | Liquid | mm | ø 6.35 |  |  | ø 6.35
|  | Gas | mm | ø 9.52 |  |  | ø 9.52
| Connections Method | Indoor / Outdoor | - | Flared / Flared |  |  | Flared / Flared
Drain Hose Size |  | O.D, I.D | mm | 21.5, 16 |  |  | 21.5, 16
Between Indoor & Outdoor | Piping Length | Min / Standard / Max | m | 3 / 7.5 / 20 |  |  | 3 / 7.5 / 20
|  | No Charge | m | 12.5 |  |  | 12.5
| Max. Elevation Difference |  | m | 10 |  |  | 10
| Piping Connection Heat Insulation |  | - | Both liquid and gas pipes |  |  | Both liquid and gas pipes
Refrigerant |  | Type | - | R32 |  |  | R32
|  | Pre Charge | kg | 1.150 |  |  | 1.150
|  | Additional Charge | g/m | 15 |  |  | 15
|  | Control | - | Electronic Expansion Valve |  |  | Electronic Expansion Valve
|  | Global Warning Potential | - | 675 |  |  | 675
|  | t-CO₂ eq | - | 0.776 |  |  | 0.776
Defrost Method |  |  | - | Reverse Cycle |  |  | Reverse Cycle
Tool Code (Chassis) |  | Indoor / Outdoor | - | S1 / U24A |  |  | S1 / U24A
Compressor | Type |  | - | Twin Rotary |  |  | Twin Rotary
| Model |  | - | DKT176MBH |  |  | DKT176MBH
| Motor Type |  | - | BLDC |  |  | BLDC
| Oil Type / Maker |  | - | FW68D or FW68L / IDEMITSU |  |  | FW68D or FW68L / IDEMITSU
| Oil Charge |  | cc | 470 |  |  | 470
| O.L.P. Name |  | - | - |  |  | -
| Manufacturer / Country of Origin |  | - | LG Electronics / China |  |  | LG Electronics / China
Fan(Indoor) | Type |  | - | Cross Flow Fan |  |  | Cross Flow Fan
| Motor Output |  | W | 30 |  |  | 30
Fan(Outdoor) | Type |  | - | Propeller Fan |  |  | Propeller Fan
| Motor Type |  | - | BLDC |  |  | BLDC
| Motor Output |  | W | 124 |  |  | 124
| Motor Insulation |  | - | Class E |  |  | Class E
| Motor Enclosure / Ingress Protection |  | - | TEAO / IPX4 |  |  | TEAO / IPX4
Heat Exchanger | Evaporator | Material, Tube / Fin | - | Cu / Al |  |  | Cu / Al
|  | (ø x Row x Column x FPI x L) x Qty. | #1 | (ø 7 x 3 x 16 x 20 x 686.6) x 1 |  |  | (ø 7 x 3 x 16 x 20 x 686.6) x 1
|  | (ø x Row x Column x FPI x L) x Qty. | #2 | - |  |  | -
|  | (ø x Row x Column x FPI x L) x Qty. | #3 | - |  |  | -
|  | (ø x Row x Column x FPI x L) x Qty. | #4 | - |  |  | -
|  | Corrosion Protection | - | PCM |  |  | PCM
|  | Fin Type | - | Slit |  |  | Slit
| Condenser | Material, Tube / Fin | - | Cu / Al |  |  | Cu / Al
|  | (ø x Row x Column x FPI x L) x Qty. | #1 | (ø 7 x 2 x 28 x 18 x 938) x 1 |  |  | (ø 7 x 2 x 28 x 18 x 938) x 1
|  | (ø x Row x Column x FPI x L) x Qty. | #2 | - |  |  | -
|  | Corrosion Protection | - | Gold |  |  | Gold
|  | Fin Type | - | Corrugate |  |  | Corrugate

## Function
Function List
Category | Function |  | NH12SP.SS1 | NH09SP.SS1
|  |  | S3-W12121CA.EC6GEEU | S3-W09121CA.EC6GEEU
Air Flow | Air Supply Outlet |  | 2 | 2
| Airflow Direction Control (Left & Right) |  | 5 Steps | 5 Steps
| Airflow Direction Control (Up & Down) |  | 6 Steps | 6 Steps
| Auto Swing (Left & Right) |  | O | O
| Auto Swing (Up & Down) |  | O | O
| Fan Speed Steps (Fan / Cool / Heat) |  | 6 / 6 / 6 | 6 / 6 / 6
| Natural Wind (Auto Wind) |  | O | O
| Jet Cool / Jet Heat (Power Wind) |  | O / O | O / O
| Comfort Air |  | X | X
| Soft Air |  | O | O
| Vane Type |  | Dual Vane | Dual Vane
| AI Air |  | O | O
Air Purifying | Prefilter (Washable / Anti-Bacteria) |  | O | O
| Deodorizing Filter |  | X | X
| Micro Dust Filter |  | X | X
| Allergy Filter |  | O | O
| Plasma Air Purifier (Ionizer) |  | O | O
Installation | Drain Pump |  | X | X
Reliability | Hot Start |  | O | O
| Self Diagnosis |  | O | O
| De-ice Control (Defrost) |  | O | O
| Dry (Dehumidification) Operation |  | O | O
Convenience | Auto Changeover |  | O | O
| Auto Operation (Artificial Intelligence) |  | X | X
| Auto Cleaning (Coil Dry) |  | O | O
| Auto Restart Operation |  | O | O
| Child Lock ¹ |  | O | O
| Forced Operation |  | O | O
| Group Control ¹ |  | X | X
| Sleep Mode |  | 12hr | 12hr
| Timer 24hr (On/Off) / 7hr (Off) |  | O / X | O / X
| Timer (Weekly) ¹ |  | O | O
| Two Thermistor Control ¹ |  | O | O
| Low Ambient Operation |  | O | O
| Overheating Protection |  | O | O
| Low Heating |  | O | O
| Voice Control |  | X | X
| Outdoor Silent Mode |  | O | O
| Mosquito Away |  | X | X
| Smart Diagnosis |  | O | O
| Indoor Unit Display Type |  | Number Display | Number Display
| Indoor Unit Display Light |  | On/Off | On/Off
| Energy Display |  | O (ThinQ only) | O (ThinQ only)
| Air Quality Indicator (Dust Sensor) |  | X | X
| Human Detecting Sensor |  | O | O
| Freeze Cleaning |  | O | O
| Window Open Detecting |  | O (ThinQ only) | O (ThinQ only)
Energy Saving | Energy Saving |  | X | X
| Energy Control |  | Active Energy Control | Active Energy Control
| Gen Mode |  | X | X
Individual Control | Wired Remote Controller (Premium) ² |  | X | X
| Wired Remote Controller (Standard) ² |  | PQRCVSL0(QW) / PREMTB(0/B)01 | PQRCVSL0(QW) / PREMTB(0/B)01
| Wired Remote Controller (Simple with Mode Selection) ² |  | PQRCVCL0Q(W) | PQRCVCL0Q(W)
| Wired Remote Controller (Simple without Mode Selection) ² |  | PQRCHCA0Q(W) | PQRCHCA0Q(W)
| Handheld Wireless Controller | (See Remote Controller Section) | AKB30086101 | AKB30086101
|  | Setting Temperature Range (Cooling) | 18~30 °C (64~86 °F) | 18~30 °C (64~86 °F)
|  | Setting Temperature Range (Heating) | 16~30 °C (60~86 °F) | 16~30 °C (60~86 °F)
CAC Network Function | General Central Controller (Non LGAP) |  | X | X
| Network Solution (LGAP) |  | O | O
| Dry Contact ² |  | PDRYCB000, PDRYCB100, PDRYCB400, PDRYCB500 | PDRYCB000, PDRYCB100, PDRYCB400, PDRYCB500
| PDI (Power Distribution Indicator) ² |  | X | X
| Outdoor Unit PI 485 ² |  | PMNFP14A1 | PMNFP14A1
Special Function Kit | Wi-Fi ² |  | Embedded | Embedded
| Water Level Sensor Connection ² |  | X | X
| Wind Baffle Kit ² |  | X | X
| Sump Heater |  | X | X
| Sheath Heater ² |  | O | O
| Crank Case Heater |  | O | O
| Smart Inverter Monitoring System (SIMs) ² |  | X | X
Others | Mode Lock |  | Cooling Only or Heating Only | Cooling Only or Heating Only
| DRED (Demand Response Enabling Device) |  | X | X
Hygiene | UV Nano |  | X | X
Note on B10: Step that can be adjusted only with Fan Speed Key (Power wind is not included because there is a separate key)
Note on B34: CSA Comfort Sleep : Comfort Sleep (7hr) ME Comfort Sleep : Comfort Sleep (Continuous)
Note on B35: 7hr (Off) : Mean Simple Timer

## Capacity_C
Capacity Table_Rated Cooling Capacity
NH09SP.SS1 (S3-W09121CA.EC6GEEU)
Outdoor Air Temperature | Indoor Air Temperature : ˚C DB / ˚C WB
| 18 / 12 |  |  | 20 / 14 |  |  | 22 / 16 |  |  | 25 / 18 |  |  | 27 / 19 |  |  | 29 / 19 |  |  | 32 / 23
˚C DB | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI
-15 | 2.61 | 2.08 | 0.4 | 3.27 | 2.21 | 0.48 | 3.92 | 2.35 | 0.55 | 4.74 | 2.51 | 0.64 | 5.23 | 2.61 | 0.7 | 5.49 | 3.37 | 0.72 | 5.84 | 4.41 | 0.76
-10 | 2.7 | 2.16 | 0.42 | 3.37 | 2.3 | 0.5 | 4.05 | 2.44 | 0.58 | 4.89 | 2.62 | 0.67 | 5.4 | 2.72 | 0.73 | 5.66 | 3.51 | 0.76 | 6.02 | 4.59 | 0.8
-5 | 2.89 | 2.32 | 0.42 | 3.48 | 2.47 | 0.5 | 4.07 | 2.62 | 0.59 | 4.8 | 2.81 | 0.7 | 5.24 | 2.92 | 0.76 | 5.53 | 3.58 | 0.8 | 5.93 | 4.49 | 0.85
-1 | 3.05 | 2.45 | 0.46 | 3.6 | 2.58 | 0.54 | 4.14 | 2.72 | 0.62 | 4.82 | 2.89 | 0.71 | 5.23 | 2.99 | 0.77 | 5.51 | 3.6 | 0.81 | 5.91 | 4.43 | 0.86
0 | 3.1 | 2.49 | 0.47 | 3.63 | 2.62 | 0.55 | 4.16 | 2.75 | 0.62 | 4.82 | 2.91 | 0.72 | 5.22 | 3.01 | 0.77 | 5.51 | 3.6 | 0.81 | 5.9 | 4.42 | 0.86
4 | 3.28 | 2.63 | 0.52 | 3.76 | 2.74 | 0.59 | 4.24 | 2.86 | 0.65 | 4.84 | 3 | 0.74 | 5.2 | 3.08 | 0.78 | 5.49 | 3.62 | 0.82 | 5.88 | 4.35 | 0.87
10 | 3.51 | 2.81 | 0.58 | 3.92 | 2.9 | 0.64 | 4.34 | 3 | 0.69 | 4.86 | 3.11 | 0.76 | 5.18 | 3.18 | 0.8 | 5.46 | 3.64 | 0.83 | 5.85 | 4.27 | 0.88
16 | 3.73 | 3 | 0.65 | 4.09 | 3.06 | 0.69 | 4.44 | 3.13 | 0.73 | 4.89 | 3.22 | 0.78 | 5.15 | 3.27 | 0.81 | 5.43 | 3.66 | 0.84 | 5.82 | 4.19 | 0.89
18 | 3.7 | 2.97 | 0.68 | 4.04 | 3.05 | 0.72 | 4.37 | 3.14 | 0.76 | 4.79 | 3.24 | 0.81 | 5.04 | 3.3 | 0.83 | 5.33 | 3.67 | 0.87 | 5.71 | 4.17 | 0.92
20 | 3.68 | 2.95 | 0.7 | 4 | 3.04 | 0.74 | 4.33 | 3.14 | 0.77 | 4.74 | 3.25 | 0.82 | 4.98 | 3.32 | 0.85 | 5.26 | 3.67 | 0.88 | 5.65 | 4.16 | 0.93
25 | 3.14 | 2.53 | 0.61 | 3.39 | 2.64 | 0.64 | 3.65 | 2.74 | 0.67 | 3.96 | 2.87 | 0.7 | 4.15 | 2.95 | 0.73 | 4.4 | 3.22 | 0.75 | 4.73 | 3.6 | 0.79
30 | 2.58 | 2.14 | 0.52 | 2.76 | 2.24 | 0.54 | 2.95 | 2.35 | 0.56 | 3.19 | 2.49 | 0.59 | 3.33 | 2.57 | 0.6 | 3.53 | 2.78 | 0.62 | 3.81 | 3.07 | 0.65
35 | 1.99 | 1.76 | 0.42 | 2.11 | 1.87 | 0.43 | 2.24 | 1.98 | 0.45 | 2.4 | 2.11 | 0.46 | 2.5 | 2.2 | 0.48 | 2.66 | 2.35 | 0.49 | 2.88 | 2.56 | 0.51
41 | 2.4 | 2.03 | 0.87 | 2.57 | 2.18 | 0.9 | 2.74 | 2.32 | 0.92 | 2.96 | 2.5 | 0.96 | 3.09 | 2.61 | 0.98 | 3.28 | 2.77 | 1.01 | 3.54 | 3 | 1.05
46 | 2.65 | 2.18 | 1.27 | 2.85 | 2.34 | 1.31 | 3.06 | 2.51 | 1.35 | 3.31 | 2.71 | 1.4 | 3.46 | 2.84 | 1.43 | 3.67 | 3.01 | 1.48 | 3.95 | 3.24 | 1.54
48 | 2.59 | 2.12 | 1.28 | 2.78 | 2.28 | 1.32 | 2.98 | 2.45 | 1.36 | 3.23 | 2.65 | 1.41 | 3.37 | 2.77 | 1.44 | 3.58 | 2.94 | 1.49 | 3.86 | 3.17 | 1.55
NH12SP.SS1 (S3-W12121CA.EC6GEEU)
Outdoor Air Temperature | Indoor Air Temperature : ˚C DB / ˚C WB
| 18 / 12 |  |  | 20 / 14 |  |  | 22 / 16 |  |  | 25 / 18 |  |  | 27 / 19 |  |  | 29 / 19 |  |  | 32 / 23
˚C DB | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI | TC | SHC | PI
-15 | 2.61 | 2.08 | 0.4 | 3.27 | 2.21 | 0.48 | 3.92 | 2.35 | 0.55 | 4.74 | 2.51 | 0.64 | 5.23 | 2.61 | 0.7 | 5.49 | 3.37 | 0.72 | 5.84 | 4.41 | 0.76
-10 | 2.7 | 2.16 | 0.42 | 3.37 | 2.3 | 0.5 | 4.05 | 2.44 | 0.58 | 4.89 | 2.62 | 0.67 | 5.4 | 2.72 | 0.73 | 5.66 | 3.51 | 0.76 | 6.02 | 4.59 | 0.8
-5 | 2.89 | 2.32 | 0.42 | 3.48 | 2.47 | 0.5 | 4.07 | 2.62 | 0.59 | 4.8 | 2.81 | 0.7 | 5.24 | 2.92 | 0.76 | 5.53 | 3.58 | 0.8 | 5.93 | 4.49 | 0.85
-1 | 3.05 | 2.45 | 0.46 | 3.6 | 2.58 | 0.54 | 4.14 | 2.72 | 0.62 | 4.82 | 2.89 | 0.71 | 5.23 | 2.99 | 0.77 | 5.51 | 3.6 | 0.81 | 5.91 | 4.43 | 0.86
0 | 3.1 | 2.49 | 0.47 | 3.63 | 2.62 | 0.55 | 4.16 | 2.75 | 0.62 | 4.82 | 2.91 | 0.72 | 5.22 | 3.01 | 0.77 | 5.51 | 3.6 | 0.81 | 5.9 | 4.42 | 0.86
4 | 3.28 | 2.63 | 0.52 | 3.76 | 2.74 | 0.59 | 4.24 | 2.86 | 0.65 | 4.84 | 3 | 0.74 | 5.2 | 3.08 | 0.78 | 5.49 | 3.62 | 0.82 | 5.88 | 4.35 | 0.87
10 | 3.51 | 2.81 | 0.58 | 3.92 | 2.9 | 0.64 | 4.34 | 3 | 0.69 | 4.86 | 3.11 | 0.76 | 5.18 | 3.18 | 0.8 | 5.46 | 3.64 | 0.83 | 5.85 | 4.27 | 0.88
16 | 3.73 | 3 | 0.65 | 4.09 | 3.06 | 0.69 | 4.44 | 3.13 | 0.73 | 4.89 | 3.22 | 0.78 | 5.15 | 3.27 | 0.81 | 5.43 | 3.66 | 0.84 | 5.82 | 4.19 | 0.89
18 | 3.7 | 2.97 | 0.68 | 4.04 | 3.05 | 0.72 | 4.37 | 3.14 | 0.76 | 4.79 | 3.24 | 0.81 | 5.04 | 3.3 | 0.83 | 5.33 | 3.67 | 0.87 | 5.71 | 4.17 | 0.92
20 | 3.68 | 2.95 | 0.7 | 4 | 3.04 | 0.74 | 4.33 | 3.14 | 0.77 | 4.74 | 3.25 | 0.82 | 4.98 | 3.32 | 0.85 | 5.26 | 3.67 | 0.88 | 5.65 | 4.16 | 0.93
25 | 3.39 | 2.78 | 0.7 | 3.67 | 2.9 | 0.73 | 3.94 | 3.01 | 0.76 | 4.28 | 3.15 | 0.8 | 4.49 | 3.24 | 0.82 | 4.75 | 3.54 | 0.86 | 5.11 | 3.96 | 0.9
30 | 3.09 | 2.62 | 0.69 | 3.32 | 2.76 | 0.72 | 3.54 | 2.89 | 0.75 | 3.82 | 3.06 | 0.78 | 3.99 | 3.16 | 0.8 | 4.24 | 3.41 | 0.83 | 4.57 | 3.76 | 0.86
35 | 2.78 | 2.47 | 0.69 | 2.96 | 2.62 | 0.71 | 3.14 | 2.77 | 0.73 | 3.36 | 2.96 | 0.76 | 3.5 | 3.07 | 0.77 | 3.72 | 3.29 | 0.8 | 4.03 | 3.58 | 0.83
41 | 2.78 | 2.37 | 1 | 2.98 | 2.54 | 1.03 | 3.18 | 2.71 | 1.06 | 3.43 | 2.91 | 1.1 | 3.58 | 3.04 | 1.13 | 3.8 | 3.23 | 1.16 | 4.1 | 3.5 | 1.21
46 | 2.65 | 2.18 | 1.27 | 2.85 | 2.34 | 1.31 | 3.06 | 2.51 | 1.35 | 3.31 | 2.71 | 1.4 | 3.46 | 2.84 | 1.43 | 3.67 | 3.01 | 1.48 | 3.95 | 3.24 | 1.54
48 | 2.59 | 2.12 | 1.28 | 2.78 | 2.28 | 1.32 | 2.98 | 2.45 | 1.36 | 3.23 | 2.65 | 1.41 | 3.37 | 2.77 | 1.44 | 3.58 | 2.94 | 1.49 | 3.86 | 3.17 | 1.55

## Capacity_H
Capacity Table_Rated Heating Capacity
NH09SP.SS1 (S3-W09121CA.EC6GEEU)
Outdoor Air Temperature |  | Indoor Air Temperature : °C DB
|  | 16 |  | 18 |  | 20 |  | 21 |  | 22 |  | 24 |  | 30
°C DB | °C WB | TC | PI | TC | PI | TC | PI | TC | PI | TC | PI | TC | PI | TC | PI
-34 | -34.4 | 3.02 | 3.95 | 2.93 | 4 | 2.9 | 4 | 2.87 | 3.92 | 2.85 | 3.92 | 2.79 | 3.91 | 2.73 | 3.91
-24 | -25 | 4.13 | 2.77 | 4.01 | 2.8 | 3.97 | 2.8 | 3.93 | 2.74 | 3.9 | 2.74 | 3.81 | 2.74 | 3.73 | 2.74
-19 | -20 | 4.77 | 2.85 | 4.62 | 2.83 | 4.58 | 2.83 | 4.53 | 2.8 | 4.5 | 2.8 | 4.4 | 2.77 | 4.3 | 2.77
-14 | -15 | 5.74 | 3.28 | 5.56 | 3.25 | 5.51 | 3.25 | 5.45 | 3.21 | 5.41 | 3.21 | 5.3 | 3.18 | 5.18 | 3.18
-9 | -10 | 6.18 | 3.42 | 5.99 | 3.39 | 5.93 | 3.39 | 5.87 | 3.35 | 5.83 | 3.35 | 5.71 | 3.32 | 5.58 | 3.32
-4 | -5 | 6.18 | 3.13 | 5.99 | 3.1 | 5.93 | 3.1 | 5.87 | 3.07 | 5.83 | 3.07 | 5.71 | 3.04 | 5.57 | 3.04
1 | 0 | 5.8 | 2.28 | 5.62 | 2.26 | 5.57 | 2.26 | 5.51 | 2.23 | 5.47 | 2.23 | 5.36 | 2.21 | 5.23 | 2.21
2 | 1 | 5.73 | 2.12 | 5.56 | 2.1 | 5.5 | 2.1 | 5.45 | 2.08 | 5.4 | 2.08 | 5.3 | 2.06 | 5.17 | 2.06
7 | 6 | 4.17 | 0.84 | 4.04 | 0.83 | 4 | 0.83 | 3.96 | 0.82 | 3.93 | 0.82 | 3.85 | 0.81 | 3.76 | 0.81
12 | 11 | 5.83 | 1.62 | 5.66 | 1.6 | 5.6 | 1.6 | 5.54 | 1.58 | 5.5 | 1.58 | 5.39 | 1.57 | 5.26 | 1.57
18 | 14 | 6.08 | 1.66 | 5.9 | 1.65 | 5.84 | 1.65 | 5.78 | 1.63 | 5.73 | 1.63 | 5.62 | 1.61 | 5.49 | 1.61
24 | 18 | 6.28 | 1.71 | 6.09 | 1.69 | 6.03 | 1.69 | 5.97 | 1.68 | 5.92 | 1.68 | 5.81 | 1.66 | 5.67 | 1.66
NH12SP.SS1 (S3-W12121CA.EC6GEEU)
Outdoor Air Temperature |  | Indoor Air Temperature : °C DB
|  | 16 |  | 18 |  | 20 |  | 21 |  | 22 |  | 24 |  | 30
°C DB | °C WB | TC | PI | TC | PI | TC | PI | TC | PI | TC | PI | TC | PI | TC | PI
-34 | -34.4 | 3.02 | 3.95 | 2.93 | 4 | 2.9 | 4 | 2.87 | 3.92 | 2.85 | 3.92 | 2.79 | 3.91 | 2.73 | 3.91
-24 | -25 | 4.13 | 2.77 | 4.01 | 2.8 | 3.97 | 2.8 | 3.93 | 2.74 | 3.9 | 2.74 | 3.81 | 2.74 | 3.73 | 2.74
-19 | -20 | 4.77 | 2.85 | 4.62 | 2.83 | 4.58 | 2.83 | 4.53 | 2.8 | 4.5 | 2.8 | 4.4 | 2.77 | 4.3 | 2.77
-14 | -15 | 5.74 | 3.28 | 5.56 | 3.25 | 5.51 | 3.25 | 5.45 | 3.21 | 5.41 | 3.21 | 5.3 | 3.18 | 5.18 | 3.18
-9 | -10 | 6.18 | 3.42 | 5.99 | 3.39 | 5.93 | 3.39 | 5.87 | 3.35 | 5.83 | 3.35 | 5.71 | 3.32 | 5.58 | 3.32
-4 | -5 | 6.18 | 3.13 | 5.99 | 3.1 | 5.93 | 3.1 | 5.87 | 3.07 | 5.83 | 3.07 | 5.71 | 3.04 | 5.57 | 3.04
1 | 0 | 5.8 | 2.28 | 5.62 | 2.26 | 5.57 | 2.26 | 5.51 | 2.23 | 5.47 | 2.23 | 5.36 | 2.21 | 5.23 | 2.21
2 | 1 | 5.73 | 2.12 | 5.56 | 2.1 | 5.5 | 2.1 | 5.45 | 2.08 | 5.4 | 2.08 | 5.3 | 2.06 | 5.17 | 2.06
7 | 6 | 4.17 | 0.84 | 4.04 | 0.83 | 4 | 0.83 | 3.96 | 0.82 | 3.93 | 0.82 | 3.85 | 0.81 | 3.76 | 0.81
12 | 11 | 5.83 | 1.62 | 5.66 | 1.6 | 5.6 | 1.6 | 5.54 | 1.58 | 5.5 | 1.58 | 5.39 | 1.57 | 5.26 | 1.57
18 | 14 | 6.08 | 1.66 | 5.9 | 1.65 | 5.84 | 1.65 | 5.78 | 1.63 | 5.73 | 1.63 | 5.62 | 1.61 | 5.49 | 1.61
24 | 18 | 6.28 | 1.71 | 6.09 | 1.69 | 6.03 | 1.69 | 5.97 | 1.68 | 5.92 | 1.68 | 5.81 | 1.66 | 5.67 | 1.66